## Slide 1
ITEMS | PRP | EPS
Power | 632kVA | 688kVA
Power | 506kW | 550kW
Frequency / Phase / Power factor | 50Hz / 3P / PF0.8 | 
Standard voltage | 400/230V | 
Available voltage | 380/220V · 415/240V | 
Industrial Range Powered By Cummins
PERFORMANCE DATA |  | 
Engine brand |  | DEUTZ
Engine model |  | D17
Fuel |  | Diesel
Aspiration |  | Turbo, CAC
Cooling |  | Water-cooled
Governor |  | Electronic
Cyl arrangement |  | 6L
Application |  | Prime & Standby
Fuel consumption | 100% ESP(L/H) 100% PRP(L/H) 75% PRP(L/H) 50% PRP(L/H) | 115.1 105.8 85.0 57.1
Standards : 2006/42/EC Machinery safety, 2006/95/EC Low voltage, EN 60204-1 : 2006+A1 : 2009, EN ISO 12100 : 2010, EN ISO 8528-13: 2016, ENISO 13849-1 : 2015, EN 60204-1 : 2018
PRP: Prime power is available for an unlimited number of annual operating hours in variable load applications , in accordance with ISO 8528-1.
ESP : The standby power rating is applicable for suppling emergency power in variable load applications in accordance with ISO 8528-1.overload is not allowed.
Conditions : According to the standard, the nominal power assigned by the genset is given for 25°C air inlet temperature, of a barometric pressure of 100 kPA (100 m A.S.L), and 30 % relative humidity.
NOTE：Weights and dimensions based on standard products. According to 2000/14/CE , sound data is provided at 7m for 75% prime power. For actual installation, please contact the manufacturer.
 | OPEN | SILENT
 | 3400*3400*340 | 4210*4210*4210
 | 3400 | 4210
 | 700 | 700
GENERAL INSTALLATION
Dimension(L*W*H) (mm)
Weight(kg)
Fuel tank(L)
Sound pressure level
ITEMS
@75% load&1m dB(A)
@75% load&7m dB(A)
——
——
GENERATOR SPECIFICATION
Water-cooled
Three Phase
50Hz
Diesel
AS500E5

## Slide 2
BASIC DATA | 
Engine brand | DEUTZ
Engine model | D17
Displacement | 16.25L
No. of cyl / arrangement | 6L
Bore x stroke | 142x171mm
Compression ratio | 18.7:1
Engine speed | 1500rpm
Engine type | 4-stroke diesel
EXHAUST SYSTEM | 
Exhaust stack gas temperature (max. ) | 560°C
Exhaust gas flow rate (max. ) | 107.5m³/min
Exhaust system backpressure (maximum allowable) | 5.0kPa
FUEL SYSTEM | 
Maximum restriction at lift pump | 19.6kPa
Max. fuel flow | 131L/H
COOLING SYSTEM | 
Radiator air flow | 540m³/min
Total oil capacity | 30L
Total coolant capacity | 27L
ENGINE SPECIFICATION
ELECTRICAL SYSTEM | 
Starter motor rated voltage | DC24V
Start battery | 2x60Ah(580CCA)
Battery charging alternator | DC24V/40A
INLET AIR | 
Air filter | Dry type
Max. combustion air Intake restriction | 5.0kPa
Combustion air inlet flow rate | 560 L/S
Max. allowable combustion air inlet temp | 50°C
BASIC DATA | 
Insulation & temperature rise | Class H/H
Excitation type | Self-excited
Winding leads | 12
Winding connections (standard) | Star
Winding pitch | Two thirds
Number of phase | Three phase
BASIC DATA | 
Type | Brushless
No. of bearings | Single bearing
Coupling system | Flexible disc
Maximum over speed | 2250 RPM
Coating type | Vacuum impregnation
IP rating | IP23
ALTERNATOR SPECIFICATION

## Slide 3
CONTROL SYSTEM
Key features
Single generator set controllercan be used in prime or standby scenarios
Manual and remote start, MRS application
Auto mains failure, AMF application
Genset power / frequency / factor / voltage / current detection
Engine/alternator/generator protections, emergency stop
Event log / running hours history/maintenance warning, LCD screen
User access management,
software and tools are easy
to use
Input or output configuration, USB communication port
MAINS
GENSET
CONTROLLER
Remote control
and Cloud services
LOAD

## Slide 4
STANDARD FEATURES
◆ Diesel engine，50 degrees radiator, brushless alternator ◆ Intelligent controller ◆ Output circuit breaker (up to1250A) ◆ Maintenance-free start battery, battery charge, battery switch ◆ Steel industrial silencer, exhaust bellows and elbows ◆ Steel chasis and anti-vibration shock absorbers ◆ Lifting and moving structure, expansion of oil and coolant discharge ◆ Moving parts protection, hot parts protection ◆ Special toolbox, delivery attached documentation
GENSET VERSION
OPTIONAL FEATURES | 
ENGINE | ◆ Water jacket preheater ◆ Oil Preheater, oil level maintainer, oil manual pump ◆ Heavy air filtration ◆ Residential silencer ◆ Remote radiator, heat exchanger
ALTERNATOR | ◆ PMG/AREP excitation system ◆ Anti-condensation heater ◆ Winding/bearing RTD ◆ Double bearing structure ◆ IP44 protection class
CONTROL SYSTEM | ◆ Synchronizing panel, remote control panel ◆ RS232/485, 4G & GPS wireless, ethernet communication card ◆ Additional digital/analog input/output ◆ Monitoring software, mobile APP ◆ Ni-Cad batteries
GENERATING SET | ◆ External fuel tank, automatic fuel feeding ◆ ATS / output / combining / distribution cabinet ◆ Load test cabinet ◆ Mobile trailer ◆ Customized design